## Slide 1: NVIDIA GPUs for AI: Components, Types and Infrastructure
CORPORATE TECHNICAL TRAINING
From the silicon inside one GPU to the data center that runs AI workloads
Trainer edition · Detailed speaker notes on every slide · ~2.5 hours
Notes: WELCOME & FRAMING (3 min) Welcome participants. Introduce yourself and the goal of the session: by the end, everyone should be able to look at an NVIDIA GPU spec sheet or an AI cluster design and understand what each part does and why it matters for AI workloads. Set expectations: this is a three-module session. Module 1 – what is physically inside a GPU (cores, memory, interconnects, board and software components). Module 2 – the GPU families and product types, and how to pick one for a workload. Module 3 – how GPUs are assembled into infrastructure for AI: servers, networks, storage, software, operations and facilities. Icebreaker: ask the room "Who has used a GPU for AI – on a laptop, in the cloud, or in our data center?" and "Who has had a job fail with 'CUDA out of memory'?" Use the answers to calibrate depth. Note: performance figures in this deck are approximate values from public NVIDIA datasheets and are given for comparison and teaching. Always check the current datasheet before quoting numbers to customers or using them in purchasing decisions.

## Slide 2: Agenda
Three modules, each building on the one before
01
NVIDIA GPU components
CPU vs GPU design philosophy
GPC, SM, CUDA, Tensor and RT cores
Memory hierarchy and HBM
NVLink, NVSwitch, PCIe, form factors
Board, firmware and software stack
~55 min
02
NVIDIA GPU types
Architecture generations, Pascal to Rubin
Product families by segment
Decoding product names
Data center GPU comparison
Matching GPUs to workloads
~40 min
03
GPU infrastructure for AI
The AI factory stack
DGX, HGX, MGX and cloud
Networking, storage, software
GPU sharing, sizing, monitoring
Power, cooling, deployment models
~55 min
Notes: AGENDA (2 min) Walk the three columns left to right and explain the logic: we go from the smallest unit (one GPU chip) outwards to the biggest (a data center full of them). Module 1 is the vocabulary module – once people know what an SM, a Tensor Core, HBM and NVLink are, everything later makes sense. Module 2 answers "which GPU?" – there are many product lines and the names are confusing; we will decode them. Module 3 answers "how do we run AI on them at scale?" – it covers servers, networking, storage, software, sharing, sizing, monitoring and power. Timing guidance: plan a 10-minute break between Module 2 and Module 3. Knowledge-check questions are at the end; you can also use them as spot checks after each module.

## Slide 3: Learning objectives
By the end of this session participants will be able to:
Explain the components of a GPU
Describe SMs, CUDA and Tensor Cores, the memory hierarchy and interconnects, and what each one does for AI.
Tell the GPU families apart
Place any NVIDIA GPU in its architecture and segment, and read a product name like GB200 NVL72.
Match GPUs to workloads
Choose a suitable GPU class for training, fine-tuning, inference, graphics or edge use cases.
Describe an AI infrastructure stack
Explain how servers, fabrics, storage, orchestration and facilities fit together.
Size and operate GPU capacity
Estimate GPU memory for an LLM, pick a sharing strategy and know which health metrics to watch.
Notes: LEARNING OBJECTIVES (2 min) Read the objectives aloud and point out that they are action verbs: explain, tell apart, match, describe, size and operate. These are what the knowledge check at the end tests. Audience note: the content works for infrastructure engineers, DevOps/platform engineers, solution architects and technical pre-sales. No CUDA programming is needed. Basic familiarity with servers, networking and containers helps in Module 3. Ask participants to note one question they want answered by the end; collect these on a flip chart and revisit them in the Q&A.

## Slide 4: NVIDIA GPU components
01
What is physically inside a GPU, and why each part matters for AI workloads
Notes: MODULE 1 INTRO (1 min) Transition: "Before we compare products or design clusters, we need a shared vocabulary. In this module we open up the GPU and look at each component." Key message for the module: AI performance is set by three things working together – compute (how many maths operations per second), memory (how fast data can be fed to the compute), and interconnect (how fast GPUs can talk to each other). Every component we look at belongs to one of these three groups. Ask learners to sort each component into one of them as we go.

## Slide 5: Why GPUs? CPU latency vs GPU throughput
Different design goals lead to very different silicon
CPU: a few powerful cores
Core
Core
Core
Core
Large caches
Control logic
Tens of complex cores with branch prediction and out-of-order execution
Built to finish one task as fast as possible
GPU: thousands of simpler cores
Thousands of cores run the same instruction on different data (SIMT)
Built to finish millions of small tasks at the same time
AI training and inference are mostly huge matrix multiplications, the kind of parallel maths GPUs were built for.
Notes: CPU vs GPU (5 min) Start with the design philosophy, because every later component follows from it. CPU = latency-optimized. A server CPU has tens of large cores (e.g. 32–128). Each core has deep pipelines, branch prediction, out-of-order execution and big caches. The goal is to make ONE thread finish as quickly as possible. Ideal for operating systems, databases, business logic and branchy code. GPU = throughput-optimized. A data center GPU has thousands of small cores (an H100 SXM has 16,896 FP32 CUDA cores across 132 SMs). Each core is simple. They run in groups of 32 threads called a "warp" and all threads in a warp execute the same instruction on different data – NVIDIA calls this SIMT (Single Instruction, Multiple Threads). Most of the chip area goes to arithmetic rather than control logic. Why this matters for AI: a neural network layer is essentially Y = W·X + b – a large matrix multiplication. Multiplying a 4096×4096 matrix needs about 137 billion multiply-adds, and almost all of them are independent of each other. That is perfect for a GPU. Analogy for the class: a CPU is a few expert chefs who can cook any complex dish quickly; a GPU is a stadium kitchen with thousands of cooks each making the same sandwich – it wins when you need 50,000 sandwiches. Important: GPUs do not replace CPUs. Every GPU server still has CPUs that run the OS, feed data, launch GPU kernels and handle networking and storage.

## Slide 6: Anatomy of a modern data center GPU
Simplified block diagram, modelled on the Hopper H100 (GH100) die
PCIe Gen5 host interface
GigaThread engine (work scheduler)
HBM
HBM
HBM
HBM
HBM
HBM
GPC 0
GPC 1
GPC 2
GPC 3
GPC 4
GPC 5
GPC 6
GPC 7
L2 cache (50 MB) + crossbar
NVLink 4: 18 links, 900 GB/s
Memory controllers · copy engines · NVDEC
GPCs and SMs (compute)
Graphics Processing Clusters group the Streaming Multiprocessors (small squares). A full GH100 has 144 SMs; the H100 SXM product enables 132.
L2 cache
Shared by all SMs. It reduces trips to HBM and keeps data close to the cores.
HBM stacks
High Bandwidth Memory sits beside the die on the same package: 80 GB at 3.35 TB/s on H100 SXM.
Host interface and scheduler
PCIe links to the CPU; the GigaThread engine hands thread blocks to free SMs.
NVLink
Direct GPU-to-GPU links, about 7x the bandwidth of PCIe Gen5.
Notes: GPU ANATOMY (6 min) This is a simplified view of NVIDIA's Hopper GH100 chip, the silicon inside H100. Other generations follow the same pattern with different counts. Walk the diagram from outside to inside: 1. Host interface (PCIe Gen5 x16): how the GPU connects to the server CPU. Commands, data copies and kernel launches come in here. 2. GigaThread engine: the global scheduler. A GPU program (a "kernel") is split into thread blocks; this engine assigns blocks to whichever SM is free. 3. GPCs – Graphics Processing Clusters. The die is divided into GPCs, each holding several TPCs (Texture Processing Clusters), and each TPC holds 2 SMs. Full GH100: 8 GPCs, 72 TPCs, 144 SMs. The shipping H100 SXM enables 132 SMs. Disabling a few SMs is normal practice because it improves manufacturing yield. 4. SMs – Streaming Multiprocessors – the small green squares. This is where the maths happens. Next slide goes inside one. 5. L2 cache – 50 MB on H100, shared by all SMs over a crossbar. It acts as a buffer between the SMs and HBM. 6. HBM – High Bandwidth Memory. The DRAM dies are stacked vertically and placed on the same package as the GPU die (2.5D packaging using CoWoS). That is how GPUs reach terabytes per second, versus about 0.3–0.5 TB/s for a dual-socket CPU's DDR5. 7. NVLink – 18 NVLink 4 links per H100 give 900 GB/s of total bidirectional GPU-to-GPU bandwidth. 8. Also on the die: copy engines (DMA), video decoders (NVDEC) and JPEG decoders (NVJPG), which help vision pipelines. Teaching tip: ask "If an AI job is slow, which of these boxes could be the bottleneck?" Expected answers: SMs (compute-bound), HBM (memory-bound), NVLink/PCIe (communication-bound).

## Slide 7: Inside a Streaming Multiprocessor (SM)
The SM is the GPU's basic building block; an H100 SXM has 132 of them
Streaming Multiprocessor (Hopper)
Warp scheduler + dispatch
Register file · 64 KB
CUDA cores
FP32 · INT32 · FP64
Tensor Core
(4th gen)
LD/ST units · SFUs
Warp scheduler + dispatch
Register file · 64 KB
CUDA cores
FP32 · INT32 · FP64
Tensor Core
(4th gen)
LD/ST units · SFUs
Warp scheduler + dispatch
Register file · 64 KB
CUDA cores
FP32 · INT32 · FP64
Tensor Core
(4th gen)
LD/ST units · SFUs
Warp scheduler + dispatch
Register file · 64 KB
CUDA cores
FP32 · INT32 · FP64
Tensor Core
(4th gen)
LD/ST units · SFUs
256 KB L1 data cache / shared memory · Tensor Memory Accelerator (TMA)
Warp scheduler
Picks a ready warp of 32 threads each clock. Switching warps hides memory latency.
Register file
The fastest storage on the chip, private to each thread. 256 KB per SM.
CUDA cores
General-purpose FP32, INT32 and FP64 units: one operation per clock per core.
Tensor Cores
Matrix-multiply engines: a whole small matrix multiply-accumulate (D = A×B + C) per instruction.
L1 / shared memory
Fast on-chip scratchpad that threads in a block share; the key to fast kernels like FlashAttention.
Notes: INSIDE AN SM (6 min) Each SM is like a small processor of its own. In Hopper, an SM is split into 4 processing blocks (sub-partitions). Each block has: • A warp scheduler and dispatch unit – picks one warp (32 threads) that is ready and issues its next instruction. Each SM can hold up to 64 resident warps (2,048 threads). When one warp waits for memory, the scheduler switches to another at no cost. This is how GPUs hide memory latency – through massive parallelism rather than big caches. • A 64 KB slice of the register file (256 KB per SM = 65,536 32-bit registers). Registers are the fastest storage on the GPU. • CUDA cores: 32 FP32 units, 16 INT32 units and 16 FP64 units per sub-partition (128 FP32 cores per SM). These run general maths: activations, normalization, indexing, and scientific FP64 code. • One Tensor Core per sub-partition (4 per SM) – the AI workhorse, covered on the next slide. • Load/store units and Special Function Units (SFUs: sin, cos, exp, reciprocal square root – used by softmax and GELU). Shared across the SM: 256 KB of combined L1 data cache and shared memory (configurable, up to 228 KB as shared memory). Shared memory is a programmer-managed scratchpad – optimized kernels such as FlashAttention load tiles of data here once and reuse them many times, avoiding slow trips to HBM. Hopper also added the Tensor Memory Accelerator (TMA), which copies large blocks of data between HBM and shared memory asynchronously, freeing threads to do maths. Blackwell continues this design and adds dedicated "Tensor Memory" for its 5th-generation Tensor Cores. Key takeaway: GPU performance = many SMs × many warps in flight × keeping the Tensor Cores fed with data.

## Slide 8: Three kinds of cores: CUDA, Tensor and RT
Specialized units do specialized work; for AI, Tensor Cores do most of the heavy lifting
CUDA cores
General-purpose parallel maths
Operation: one scalar FP32/INT32/FP64 operation per clock
AI role: activations, normalization, data preparation, custom kernels
Also used for: HPC simulation (FP64), graphics shading
H100 SXM: 16,896 FP32 cores
Tensor Cores
Dense matrix multiply-accumulate
Operation: a whole small matrix multiply-accumulate per instruction
AI role: the matrix multiplications in training and inference
Precisions: FP64, TF32, BF16, FP16, FP8, INT8, FP6, FP4 (varies by generation)
H100 SXM: 528 Tensor Cores
RT cores
Ray-tracing acceleration
Operation: ray / triangle intersection and BVH traversal
AI role: none directly; used for rendering, simulation and digital twins
Found in: RTX, L40S, L4; not in H100, H200 or B200
L40S: 142 3rd-gen RT cores
Notes: THREE CORE TYPES (5 min) CUDA cores: the general-purpose workers. One CUDA core does one floating-point or integer operation per clock (a fused multiply-add counts as 2 FLOPs). Much of a model's code that is NOT a big matrix multiply – activation functions, layer normalization, softmax, data augmentation, custom kernels – runs on CUDA cores. Tensor Cores: introduced with Volta (V100) in 2017. Instead of one multiply per clock, a Tensor Core performs a whole small matrix multiply-accumulate (D = A×B + C) in one instruction. This is why an H100 delivers about 67 TFLOPS of plain FP32 on CUDA cores but about 990 TFLOPS of dense BF16/FP16 and about 1,979 TFLOPS of dense FP8 on Tensor Cores – an order of magnitude more. Frameworks like PyTorch use Tensor Cores automatically through cuBLAS and cuDNN when you use mixed precision (BF16/FP16) or TF32. RT cores: introduced with Turing (2018). They accelerate ray tracing – testing whether light rays hit triangles in a 3D scene. They are not used for neural network maths. They matter for "visual computing + AI" workloads: Omniverse digital twins, rendering, synthetic data generation for robotics, and virtual workstations. That is why the L40S and RTX PRO GPUs have RT cores while the H100/H200/B200 training GPUs do not – they spend that silicon on more Tensor Cores and FP64. Discussion question: "Why might a company choose an L40S over an H100 for a mixed rendering + inference farm?" (Answer: RT cores, graphics/display features, lower power, PCIe form factor, lower cost.)

## Slide 9: Tensor Core generations and number formats
Each generation adds lower-precision formats, which roughly doubles throughput and halves memory per value
Architecture (year) | Tensor Core gen | Formats added | What it enabled
Volta (2017) | 1st | FP16 with FP32 accumulate | Mixed-precision training became mainstream
Turing (2018) | 2nd | INT8, INT4 | Low-cost, high-throughput inference (T4)
Ampere (2020) | 3rd | TF32, BF16, FP64, 2:4 sparsity | FP32-like training with no code change (TF32)
Hopper (2022) | 4th | FP8 (E4M3 / E5M2), Transformer Engine | FP8 training and inference for transformers
Blackwell (2024) | 5th | FP6, FP4, MXFP microscaling, NVFP4 | 4-bit inference, 2nd-generation Transformer Engine
Why lower precision?
FP32
BF16
FP8
FP4
Half the bits = half the memory and bandwidth per value
About 2x the Tensor Core throughput
Transformer Engine picks FP8 or FP16 per layer to protect accuracy
Formats are cumulative: newer generations keep supporting the older formats.
Notes: PRECISION FORMATS (6 min) This is one of the most important ideas in AI hardware: precision is a performance lever. Walk the table: • Volta: first Tensor Cores; FP16 multiply with FP32 accumulate. Introduced "mixed-precision training" – keep a master copy of the weights in FP32, compute in FP16. • Turing: added INT8 and INT4 for inference. The T4 (70 W) became the cloud inference workhorse for years. • Ampere: added TF32 – a 19-bit format with FP32's range and FP16-like precision. Frameworks can use it automatically, so FP32 code gets Tensor Core speed without changes. Also BF16 (FP32 range, less precision – now the standard training format), FP64 Tensor Cores for HPC, and 2:4 structured sparsity (up to 2x if half the weights are zero in a fixed pattern). Note: datasheet numbers quoted "with sparsity" are double the dense numbers – always compare dense with dense. • Hopper: FP8 in two flavours – E4M3 (more precision, used in the forward pass) and E5M2 (more range, used for gradients). The Transformer Engine (hardware + software library) tracks value ranges per tensor and picks scaling factors so FP8 training keeps accuracy. • Blackwell: FP6 and FP4 with "microscaling" – small blocks of values share a scale factor, which keeps 4-bit accuracy usable. NVFP4 is NVIDIA's own 4-bit format; Blackwell Ultra (B300) further boosts NVFP4 throughput. Right panel: halving the bits halves memory and bandwidth per weight and roughly doubles Tensor Core throughput. A 70-billion-parameter model needs about 140 GB in BF16, 70 GB in FP8 and about 35 GB in FP4. Caveat to teach: lower precision is not free – it may need calibration, quantization-aware training or validation against accuracy benchmarks. Training typically uses BF16/FP8; inference increasingly uses FP8/FP4.

## Slide 10: The GPU memory hierarchy
Feeding the cores matters as much as the cores themselves (H100 SXM values shown)
Registers
256 KB per SM · ~1 cycle
L1 cache / shared memory
256 KB per SM · tens of cycles
L2 cache
50 MB shared · ~200 cycles
HBM3 (GPU memory)
80 GB · 3.35 TB/s
Host memory via PCIe / NVLink-C2C
TBs · 64–450 GB/s per direction
faster,
smaller
larger,
slower
Why this matters for AI
Memory-bound vs compute-bound: low arithmetic intensity means the cores sit waiting for data.
LLM token generation reads every weight for each token, so HBM bandwidth sets tokens per second.
Capacity decides whether the model, KV cache and activations fit on one GPU.
Fast kernels (FlashAttention, fused ops) keep data in SRAM to avoid HBM trips.
Notes: MEMORY HIERARCHY (6 min) Teach this as a pyramid: the closer storage is to the cores, the faster and smaller it is. • Registers: 64K × 32-bit registers per SM (256 KB). Fastest; private to each thread. • L1/shared memory: 256 KB per SM on H100. Shared memory is managed by the programmer and shared by the threads in a block. • L2: 50 MB on H100, shared by all SMs. Blackwell increases L2 again. • HBM: the "GPU memory" on the spec sheet – 80 GB HBM3 at 3.35 TB/s (H100 SXM), 141 GB HBM3e at 4.8 TB/s (H200), 180–192 GB at 8 TB/s (B200). • Host memory: reached over PCIe Gen5 (about 64 GB/s each way) or, on Grace Hopper/Grace Blackwell superchips, over NVLink-C2C (900 GB/s total). Used for offloading optimizer states or KV cache, but much slower than HBM. Key concept – arithmetic intensity = FLOPs per byte moved. An H100 can do about 1,000 dense BF16 TFLOPS but move only 3.35 TB/s, so a kernel needs roughly 300 FLOPs per byte to be compute-bound. Big training matrix multiplies reach that; many other operations do not. LLM inference example: in the "decode" phase each new token needs every weight to be read once. A 70B model in FP8 is about 70 GB; at 3.35 TB/s that is about 48 reads per second, so at most about 48 tokens/s for a single stream on one H100 (batching helps because the same weights serve many users). This is why H200's larger, faster HBM gives big inference gains with the SAME compute as H100. Takeaway: when comparing GPUs for inference, look at memory capacity and bandwidth first, not just TFLOPS.

## Slide 11: HBM capacity and bandwidth by generation
Memory has grown faster than almost any other spec, driven by large language models
Chart: Memory per GPU (GB)
| V100 | A100 | H100 | H200 | B200 | B300
Memory (GB) | 32 | 80 | 80 | 141 | 180 | 288
Chart: Memory bandwidth per GPU (TB/s)
| V100 | A100 | H100 | H200 | B200 | B300
Bandwidth (TB/s) | 0.9 | 2 | 3.35 | 4.8 | 8 | 8
Approximate SXM figures from public datasheets. B200 is shown at 180 GB as shipped in HGX/DGX B200 systems. V100 32 GB HBM2 · A100 80 GB HBM2e · H100 HBM3 · H200, B200, B300 HBM3e.
Notes: HBM TRENDS (4 min) Use the two charts to show the trend: from V100 (2017) to B300 (2025), memory per GPU grew about 9x (32 → 288 GB) and bandwidth about 9x (0.9 → 8 TB/s). Why it grew so fast: model sizes went from hundreds of millions of parameters (BERT) to hundreds of billions or trillions. LLM inference also needs a KV cache that grows with context length and the number of concurrent users. Points to make: • H100 → H200: same Hopper compute, but 141 GB HBM3e at 4.8 TB/s instead of 80 GB at 3.35 TB/s. NVIDIA reported up to roughly 1.9x faster Llama-2-70B inference – a pure memory upgrade. • B200 uses two reticle-sized dies joined by a 10 TB/s die-to-die link (NV-HBI), with 8 HBM3e stacks for 8 TB/s. • B300 (Blackwell Ultra) moves to 12-high HBM3e stacks for 288 GB. • Next: the Rubin generation is announced with HBM4. HBM is also a major part of GPU cost and supply constraints – HBM and advanced packaging capacity (CoWoS) are often what limits how many GPUs can be built. Reminder: these are approximate public figures for teaching. Exact usable memory can differ by SKU and system (e.g. B200 is listed at 180 GB usable in HGX/DGX B200).

## Slide 12: Interconnects: how GPUs talk to CPUs and to each other
Multi-GPU AI is only as fast as the links between GPUs
PCIe Gen5 x16
128 GB/s
total, both directions
GPU ↔ CPU, NICs and storage
Standard slot in any server
PCIe Gen6 doubles this on Blackwell-era platforms
NVLink 4 (Hopper)
900 GB/s
per GPU, 18 links
Direct GPU ↔ GPU
About 7x PCIe Gen5
Up to 8 GPUs per HGX H100/H200 node
NVLink 5 (Blackwell)
1.8 TB/s
per GPU, 18 links
Twice NVLink 4
Up to 72 GPUs in one NVLink domain (NVL72)
Built for trillion-parameter models
NVLink-C2C
900 GB/s
CPU ↔ GPU, coherent
Joins Grace CPU and GPU in superchips
GPU can read CPU memory directly
Used in GH200 and GB200
NVSwitch
Switch chips connect every GPU to every other GPU at full NVLink speed, with no hops through the CPU.
GPU0
GPU1
GPU2
GPU3
GPU4
GPU5
GPU6
GPU7
NVSwitch fabric (all-to-all, non-blocking)
Notes: INTERCONNECTS (6 min) Large models do not fit on one GPU, and training splits work across many GPUs. GPUs must constantly exchange data: gradients (all-reduce in data parallelism), activations (pipeline parallelism) and partial matrix results (tensor parallelism). The speed of these links often decides how well a job scales. • PCIe Gen5 x16: about 64 GB/s each way, 128 GB/s total. Universal and fine for single-GPU inference or loosely coupled work. When GPUs talk over PCIe, traffic may cross CPU sockets, which adds latency. • NVLink 4 (Hopper): 18 links × 50 GB/s = 900 GB/s total per GPU – about 7x PCIe Gen5. • NVLink 5 (Blackwell): 1.8 TB/s per GPU. With NVLink Switch trays, 72 GPUs share one NVLink domain (GB200 NVL72) – the whole rack behaves like one giant GPU for tensor/expert parallelism. • NVLink-C2C: chip-to-chip link between Grace CPU and the GPU at 900 GB/s, cache-coherent. The GPU can use the CPU's LPDDR5X memory as an extension of its own, much faster than PCIe. NVSwitch (bottom panel): inside an HGX H100 baseboard, 4 NVSwitch chips connect all 8 GPUs so any GPU reaches any other at full 900 GB/s. HGX B200 uses 2 newer NVSwitch chips at 1.8 TB/s per GPU. NVSwitch also supports SHARP – doing reduction maths inside the switch to speed up all-reduce. PCIe-card GPUs (e.g. H100 NVL, H200 NVL) can use NVLink bridges between 2 or 4 cards, but not a full NVSwitch fabric. Practical tip: run "nvidia-smi topo -m" on a server to see whether GPU pairs connect via NVLink (NV#) or PCIe paths (PIX/PXB/PHB/SYS). We will come back to this in the operations slide.

## Slide 13: Form factors: PCIe card, SXM module, superchip
The same GPU architecture comes in different physical packages
GPU
PCIe card
Fits standard servers; air-cooled
72–600 W (e.g. L4, L40S, H100 NVL)
Optional NVLink bridge for 2–4 cards
Best for inference and mixed enterprise fleets
SXM
SXM
SXM
SXM
SXM
SXM
SXM
SXM
SXM module
Mounted on an HGX baseboard of 4 or 8 GPUs
Up to 700 W (H100) or 1,000 W+ (B200)
Full NVSwitch fabric between all GPUs
Best for training and large-model inference
Grace
CPU
Blackwell
Blackwell
Superchip
Grace CPU + GPU on one board via NVLink-C2C
GH200, GB200, GB300
Built into rack-scale NVL72 systems
Best for the largest models; liquid-cooled
Notes: FORM FACTORS (5 min) PCIe card: a standard add-in card that fits into a normal server PCIe slot. Most are passively cooled (no fan on the card; the server's fans push air through). Power ranges from 72 W (L4, low-profile, single slot) to about 350–600 W (L40S, H100 NVL, H200 NVL, RTX PRO 6000 Blackwell Server Edition). Easiest to deploy in existing enterprise data centers. Some PCIe GPUs can be paired with NVLink bridges. SXM module: a socketed module, not a slot card. SXM GPUs are mounted on an NVIDIA HGX baseboard (4 or 8 GPUs) together with NVSwitch chips. Higher power limits (700 W for H100/H200 SXM, about 1,000 W for B200, more for B300) allow higher clocks and full NVLink bandwidth. Server OEMs (Dell, HPE, Lenovo, Supermicro and others) build "HGX servers" around these baseboards; NVIDIA's own version is the DGX. Superchip: Grace CPU (72 Arm Neoverse V2 cores, LPDDR5X memory) plus one GPU (GH200) or two GPUs (GB200) on one board, joined by NVLink-C2C. These are the building blocks of rack-scale systems like GB200 NVL72 and GB300 NVL72, which are liquid-cooled. Decision guide for the class: • Existing air-cooled racks, inference, VDI, mixed workloads → PCIe. • Serious multi-GPU training or very large model serving → SXM / HGX. • Frontier-scale training and real-time inference of trillion-parameter models → superchip / NVL72.

## Slide 14: Board-level components around the GPU
Power, cooling, firmware and management: everything that keeps the GPU running 24/7
Power delivery
VRMs convert board power to core voltages
Power ranges from 72 W (L4) to 1,000 W+ (B200)
Power capping trades a little speed for efficiency
Thermal design
Passive heatsinks rely on server airflow
Direct liquid cooling for 1 kW-class GPUs
Thermal throttling cuts clocks when too hot
Firmware and GSP
VBIOS initializes the board
GPU System Processor (GSP) offloads driver tasks
Firmware updates are part of fleet patching
Reliability and security
ECC on HBM; row remapping isolates bad memory
Secure boot and signed firmware
Confidential computing on Hopper and Blackwell
Telemetry and management
NVML library and the nvidia-smi CLI
DCGM for fleet health, diagnostics and metrics
Server BMC / Redfish for out-of-band control
Partitioning hardware
Multi-Instance GPU (MIG): up to 7 isolated GPUs
Each slice gets its own SMs, cache and memory
A100, H100, H200, B200 and later
Notes: BOARD-LEVEL COMPONENTS (5 min) These are the "unglamorous" components that operations teams deal with every day. Power delivery: voltage regulator modules (VRMs) on the board convert 12 V/48 V input into the low voltages the GPU core and HBM need. Modern GPUs change power draw very quickly, which stresses power supplies – facility design must account for this. Administrators can set power limits with nvidia-smi -pl; running slightly below maximum power often keeps most of the performance at better efficiency. Thermal: data center PCIe GPUs are passive and need high server airflow. SXM GPUs at 700 W are still air-coolable; Blackwell-generation 1 kW+ parts, and especially NVL72 racks, use direct-to-chip liquid cooling. When a GPU gets too hot it throttles (lowers clocks) – a silent performance killer that shows up in DCGM metrics. Firmware and GSP: the VBIOS initializes the board at power-on. Modern NVIDIA GPUs include a GPU System Processor (GSP) – a RISC-V microcontroller that runs firmware handling initialization and management tasks that used to run in the host driver. Firmware and driver versions must be managed together across the fleet. Reliability and security: HBM has ECC; when memory cells go bad, the GPU can remap rows (visible in nvidia-smi -q). Hopper introduced confidential computing (encrypting data in use on the GPU), and Blackwell extends it with TEE-I/O support. Telemetry: NVML is the C library under nvidia-smi; DCGM (Data Center GPU Manager) adds health checks, diagnostics (dcgmi diag) and a Prometheus exporter for Kubernetes. The server's BMC gives out-of-band power, temperature and inventory data. MIG: introduced with A100. Hardware-level partitioning into up to 7 instances, each with dedicated SMs, L2 slices and memory. We cover sharing strategies in Module 3.

## Slide 15: The software stack that makes the hardware useful
From the driver up to AI platforms: NVIDIA's real advantage is the full stack
AI platforms and services
NeMo · NIM microservices · Triton Inference Server · Dynamo · RAPIDS
Frameworks
PyTorch · JAX · TensorFlow · vLLM · SGLang · TensorRT-LLM
CUDA-X libraries
cuBLAS · cuDNN · NCCL · TensorRT · CUTLASS · cuDF
CUDA toolkit and runtime
nvcc compiler · CUDA runtime API · Nsight profilers
Driver and firmware
Kernel driver · GSP firmware · Fabric Manager · NVML
GPU hardware
SMs · Tensor Cores · HBM · NVLink
Version compatibility
The driver must support the CUDA version your containers were built with. Pin and test versions together.
NCCL: the multi-GPU glue
All-reduce and all-gather over NVLink and InfiniBand. Its performance drives training scaling.
Containers from NGC
NVIDIA's NGC catalog publishes tested containers that bundle CUDA, libraries and frameworks.
Notes: SOFTWARE STACK (5 min) Make the point that hardware alone is useless without software. NVIDIA's long lead comes largely from CUDA (released 2006) and the ecosystem built on it. Walk bottom to top: • Hardware. • Driver and firmware: the kernel-mode driver, GSP firmware, the NVML management library, and Fabric Manager – a service required on NVSwitch systems (HGX/DGX) to configure the NVLink fabric. If Fabric Manager is not running on an HGX node, CUDA jobs will fail to start. • CUDA toolkit: the compiler (nvcc), runtime and driver APIs, and the Nsight Systems/Compute profilers. • CUDA-X libraries: cuBLAS (matrix maths), cuDNN (deep learning primitives), NCCL (collective communication across GPUs and nodes), TensorRT (inference optimization), CUTLASS (templates for custom matrix kernels), and RAPIDS cuDF (GPU dataframes). • Frameworks: PyTorch, JAX and TensorFlow call these libraries; serving engines like vLLM, SGLang and TensorRT-LLM are optimized for LLM inference. • Platforms: NeMo (building, customizing and aligning models), NIM (pre-packaged, optimized inference microservices), Triton Inference Server, and Dynamo (NVIDIA's distributed inference serving framework, introduced in 2025). Right side – three operational lessons: 1. Compatibility: each CUDA release needs a minimum driver version. CUDA forward-compatibility packages and containers help, but standardize driver versions across the fleet. 2. NCCL performance decides scaling efficiency. Use nccl-tests (all_reduce_perf) to benchmark new clusters. 3. Use containers (NGC, or your own built on NGC base images) so applications carry their CUDA userspace and the host only needs the driver plus the NVIDIA Container Toolkit. Many of these components are bundled and supported commercially as NVIDIA AI Enterprise.

## Slide 16: NVIDIA GPU types
02
Architecture generations, product families and how to choose the right GPU for a workload
Notes: MODULE 2 INTRO (1 min) Transition: "Now that we know what is inside a GPU, let's look at the different GPUs NVIDIA makes. There are two axes: the architecture generation (when it was designed and what features it has) and the market segment (data center, workstation, consumer, edge). A specific product sits at a crossing of those two axes." Goal of the module: by the end, learners can look at any product name and place it, and can recommend a GPU class for a given workload.

## Slide 17: Architecture generations at a glance
Roughly a new data center architecture every two years, now moving to a yearly cadence
2016
Pascal
P100
First HBM2 and NVLink
2017
Volta
V100
1st-gen Tensor Cores
2018
Turing
T4
INT8 / INT4 inference, RT cores
2020
Ampere
A100
TF32, BF16, MIG, sparsity
2022
Hopper
H100, H200
FP8 Transformer Engine
2022
Ada Lovelace
L40S, L4
FP8 for inference and graphics
2024
Blackwell
B200, GB200
FP4, NVLink 5, dual-die
2025
Blackwell Ultra
B300, GB300
288 GB HBM3e, faster NVFP4
2026
Rubin
Vera Rubin
HBM4, NVLink 6 (roadmap)
Architectures are named after scientists: Blaise Pascal, Alessandro Volta, Alan Turing, André-Marie Ampère, Grace Hopper, Ada Lovelace, David Blackwell and Vera Rubin.
Notes: ARCHITECTURE TIMELINE (6 min) Walk the timeline and give one headline per generation: • Pascal (2016, P100): first GPU with HBM2 and NVLink – the start of the modern data center GPU. • Volta (2017, V100): introduced Tensor Cores; the GPU that trained the first wave of transformers (BERT, GPT-2). • Turing (2018, T4): INT8/INT4 inference and RT cores; T4 at 70 W became the standard cloud inference card. • Ampere (2020, A100): TF32, BF16, structured sparsity, MIG and 3rd-gen NVLink. A100 trained GPT-3-era models and is still widely deployed. • Hopper (2022, H100; H200 in 2024): FP8 with the Transformer Engine, 4th-gen NVLink, confidential computing. The GPU of the generative-AI boom. • Ada Lovelace (2022): the graphics-plus-AI architecture – RTX 40 series, RTX 6000 Ada, L40S and L4. FP8 Tensor Cores and 3rd-gen RT cores, GDDR6 memory instead of HBM. • Blackwell (2024, B200, GB200): two dies in one package (208 billion transistors), FP4, NVLink 5 and rack-scale NVL72. Blackwell also covers RTX 50 series and RTX PRO 6000 Blackwell. • Blackwell Ultra (2025, B300, GB300): more HBM (288 GB) and faster attention and NVFP4. • Rubin (2026): announced as the next generation with the Vera CPU, HBM4 and NVLink 6. Trainer note: check the current status of Rubin products before delivering, as availability changes quickly. Point out the cadence: NVIDIA moved from roughly two-year to yearly updates. For infrastructure planners this means a cluster bought today will be 1–2 generations behind within its depreciation period – plan refresh cycles and mixed-generation fleets. Fun fact for engagement: the Grace CPU and Hopper GPU together honor Rear Admiral Grace Hopper; Vera Rubin was the astronomer whose work provided evidence for dark matter.

## Slide 18: Product families by market segment
One architecture is sold in several segments, each tuned for different buyers and duty cycles
Data center
H100, H200
B200, B300
L40S, L4
RTX PRO 6000 Server
Typical use
Training, inference, HPC, VDI
Superchip / rack scale
GH200
GB200 NVL72
GB300 NVL72
DGX GB200 / GB300
Typical use
Frontier training, very large inference
Workstation
RTX PRO 6000 Blackwell
RTX PRO 4000–5000
RTX 6000 Ada
DGX Spark / Station
Typical use
Local development, design, small fine-tunes
Consumer
GeForce RTX 5090
GeForce RTX 5080
GeForce RTX 40 series
Laptop GPUs
Typical use
Gaming, hobby and learning AI
Edge / embedded
Jetson Orin
Jetson Thor
IGX Orin
DRIVE (automotive)
Typical use
Robotics, vision, autonomous machines
Notes: PRODUCT FAMILIES (5 min) Explain that one architecture (for example Blackwell) shows up in many segments with different chips, memory types, drivers and support terms. Data center: built for 24/7 operation in servers – passive cooling, ECC memory, enterprise drivers, long-term support, virtualization (vGPU) and, on top parts, MIG and NVLink. Includes the training flagships (H100/H200/B200/B300) and "universal" PCIe GPUs like L40S, L4 and RTX PRO 6000 Blackwell Server Edition that handle inference, graphics and video. Superchip / rack scale: Grace + GPU systems. Sold as complete racks (GB200 NVL72, GB300 NVL72) or as NVIDIA DGX systems. Workstation (professional RTX, formerly "Quadro"): certified drivers for CAD/DCC applications, large memory (RTX PRO 6000 Blackwell has 96 GB GDDR7), ECC, multi-display. Increasingly used as desktop AI development machines. DGX Spark (GB10 superchip, 128 GB unified memory) and DGX Station (GB300) are desktop AI systems. Consumer (GeForce): excellent price/performance for learning and experimentation – an RTX 5090 has 32 GB GDDR7. But see the later slide: GeForce licensing and features are not intended for data center deployment. Edge / embedded: Jetson modules combine an Arm CPU and GPU in a small, low-power module for robots, drones, smart cameras and industrial systems. Jetson Orin delivers up to about 275 TOPS; Jetson Thor (Blackwell-based) targets humanoid robots. IGX is the industrial/medical-grade edge platform; DRIVE is automotive. Ask: "Which segment fits our own use cases?" – most enterprises use data center GPUs in the core plus workstations for developers.

## Slide 19: Decoding NVIDIA product names
Worked example: GB200 NVL72
G
Grace CPU
(Arm, 72 cores)
B
Blackwell
architecture
200
Tier / generation
(100, 200, 300)
NVL72
72 GPUs in one
NVLink domain
Prefix | Architecture | Examples
V / T | Volta / Turing | V100, T4
A | Ampere | A100, A10, A2
H | Hopper | H100, H200
L | Ada Lovelace (data center) | L40S, L4
B | Blackwell | B200, B300
GH / GB | Grace + Hopper / Blackwell | GH200, GB200
Suffix / term | Meaning
SXM | Socketed module on an HGX baseboard
PCIe | Standard add-in card
NVL (card) | PCIe card pairs with NVLink bridges (H100 NVL, H200 NVL)
NVL72 (rack) | Rack where 72 GPUs share one NVLink domain
Ultra / x00 | Mid-cycle upgrade, e.g. Blackwell Ultra = B300
RTX PRO / GeForce | Professional / consumer graphics lines
Notes: DECODING NAMES (5 min) Product names look cryptic but follow a pattern. Use the GB200 NVL72 example: • G = Grace (NVIDIA's Arm-based data center CPU). • B = Blackwell GPU architecture. • 200 = the tier/generation number. In the data center line, "100" was the first flagship of an architecture (A100, H100), "200" a step up (H200 = Hopper with HBM3e; GB200/B200 = first Blackwell parts) and "300" Blackwell Ultra (B300, GB300). • NVL72 = 72 GPUs connected in a single NVLink domain (one rack). Left table – architecture letters. "L" is the odd one: it stands for Ada Lovelace in data center products (L40S, L4, L40), because "A" was already used for Ampere. Small numbers mean smaller, lower-power cards (A2, L4 vs A100). Right table – suffixes: • SXM vs PCIe: same architecture, different package, power and interconnect (e.g. H100 SXM 700 W with NVSwitch vs H100 PCIe 350 W). • "NVL" on a card (H100 NVL, H200 NVL) means a PCIe card designed to be paired with NVLink bridges – a common choice for LLM inference in standard servers. • "NVL72" (or NVL36, NVL144) on a rack means the size of the NVLink domain. Note: NVIDIA has said the Rubin generation counts GPU dies rather than packages in names like "NVL144". • Professional cards use "RTX PRO" (Blackwell) or "RTX ####" (Ada, e.g. RTX 6000 Ada). Consumer cards are "GeForce RTX ##90/80/70". Exercise: show a few names and have the class decode them: H200 NVL, GH200, L40S, RTX PRO 6000 Blackwell, Jetson AGX Orin.

## Slide 20: Data center GPU comparison
Key specs side by side (approximate, per GPU)
GPU | Architecture | Memory | Bandwidth | FP8 dense | Max power | Form factor | Sweet spot
A100 | Ampere | 80 GB HBM2e | 2.0 TB/s | No FP8 | 400 W | SXM / PCIe | Installed-base training and inference
H100 | Hopper | 80 GB HBM3 | 3.35 TB/s | ~1,979 TFLOPS | 700 W | SXM (PCIe, NVL) | Training and LLM inference
H200 | Hopper | 141 GB HBM3e | 4.8 TB/s | ~1,979 TFLOPS | 700 W | SXM / NVL | Memory-hungry LLM inference
B200 | Blackwell | 180 GB HBM3e | 8 TB/s | ~4,500 TFLOPS | ~1,000 W | SXM (HGX) | Large-scale training, FP4 inference
L40S | Ada Lovelace | 48 GB GDDR6 | 864 GB/s | ~733 TFLOPS | 350 W | PCIe | Inference, fine-tuning, graphics
L4 | Ada Lovelace | 24 GB GDDR6 | 300 GB/s | ~242 TFLOPS | 72 W | PCIe low-profile | Video, vision, small-model inference
Datasheets often quote FP8/FP4 "with sparsity", which is 2x the dense figure. Compare dense numbers with dense numbers.
Notes: COMPARISON TABLE (6 min) Walk down the table and highlight the pattern rather than every number. • A100: no FP8; dense INT8 is about 624 TOPS, and dense BF16 about 312 TFLOPS. Still very common in existing clusters and clouds. • H100 SXM: about 990 TFLOPS dense BF16 and about 1,979 TFLOPS dense FP8 (datasheet "3,958" includes sparsity). The 80 GB of memory can be tight for large models. • H200: identical compute to H100 – the difference is 141 GB of HBM3e at 4.8 TB/s. Great upgrade for inference and long context. • B200: about 2.25x H100 in dense FP8 per GPU, plus FP4 (about 9 PFLOPS dense). Around 1,000 W, so it needs data center planning (power and often liquid cooling). B300 (Blackwell Ultra) adds 288 GB HBM3e and higher FP4 performance. • L40S: a "universal" PCIe card – no NVLink, GDDR6 instead of HBM, but strong FP8 and RT cores. Good for inference of models up to about 30–40B parameters (quantized), fine-tuning with LoRA, and graphics/Omniverse. • L4: 72 W, single-slot, low-profile; fits almost any server. Excellent for video analytics (AV1 encode/decode), vision models and small LLMs. Not in the table but worth naming: RTX PRO 6000 Blackwell Server Edition (96 GB GDDR7, PCIe) – the Blackwell successor to the L40S class. Warning callout: sparsity doubles the headline number. Many vendor slides compare a sparse number with someone else's dense number. Always check the footnote. Trainer note: these values are approximate public datasheet figures; refresh them before each delivery.

## Slide 21: Choosing a GPU for the workload
Start from the workload's bottleneck (compute, memory or communication), not from the newest product
Workload | Main bottleneck | Typical GPU choice | Why
Frontier / foundation model pre-training | Compute + interconnect | GB200 / GB300 NVL72, HGX B200 / B300 | Largest NVLink domains, FP8/FP4, scale-out fabric
Full fine-tuning of 30–70B+ models | Memory + interconnect | HGX H100 / H200 / B200 (8 GPUs) | NVSwitch for sharded training (FSDP / ZeRO)
LoRA / QLoRA fine-tuning | Memory | L40S, H100 NVL, RTX PRO 6000 | Adapters fit on 1–2 GPUs; PCIe is enough
High-volume LLM inference | Memory bandwidth | H200, B200, GB200 NVL72 | Large, fast HBM keeps KV cache and batch sizes up
Cost-efficient inference, vision, video | Price / performance | L4, L40S, RTX PRO 6000 Server | Low power, PCIe, video engines
Rendering, digital twins + AI | Graphics + AI | L40S, RTX PRO 6000 Blackwell | RT cores, display and graphics features
Robotics and edge inference | Power + size | Jetson Orin / Thor, IGX | Tens of watts, rugged modules
Notes: WORKLOAD MATRIX (6 min) Teach the method first: identify the workload's bottleneck, then pick the GPU. • Pre-training foundation models: needs maximum compute AND fast communication among thousands of GPUs. Rack-scale NVL72 or 8-GPU HGX nodes on a non-blocking InfiniBand/Spectrum-X fabric. • Full fine-tuning of large models: memory for weights + gradients + optimizer states (about 16 bytes per parameter with Adam in mixed precision – see the sizing slide). Shard across 8 NVSwitch-connected GPUs. • LoRA/QLoRA: only small adapter matrices are trained; the base model can be frozen and quantized. A single 48–96 GB card often suffices. • High-volume LLM inference: decode is memory-bandwidth-bound and the KV cache grows with users × context length. H200/B200 memory is the main win; NVL72 helps very large models (e.g. mixture-of-experts) with tight latency targets. • Cost-efficient inference: many enterprise models (embeddings, rerankers, 7–13B LLMs, vision) run well on L4/L40S class GPUs at a fraction of the cost and power. • Graphics + AI: Omniverse, CAD visualization, virtual workstations, synthetic data – needs RT cores. • Edge: power budgets of 10–130 W; Jetson modules. Group exercise (5 min): give three scenarios and let teams pick a GPU and justify it: 1. A bank wants a 7B chatbot for 500 internal users. (L4/L40S, or MIG slices on H100.) 2. A research lab will pre-train a 70B model from scratch. (Many HGX H200/B200 nodes on InfiniBand.) 3. A factory wants defect detection on 20 production lines. (Jetson Orin at the edge, L4 centrally.)

## Slide 22: Superchips and rack-scale systems
Grace CPUs and Blackwell GPUs joined into a single, liquid-cooled 72-GPU NVLink domain
GB200 superchip
Grace CPU
72 Arm cores
LPDDR5X
B200 GPU
B200 GPU
NVLink-C2C
900 GB/s
1 CPU + 2 GPUs
GPUs can use CPU memory coherently
GH200: 1 Grace + 1 Hopper GPU
Why rack scale?
One NVLink domain: 72 GPUs act like one big GPU for tensor and expert parallelism.
Copper NVLink spine in the rack avoids optical transceivers, saving power and cost.
Trade-off: needs ~120 kW+ per rack, liquid cooling and new facility design.
■ compute tray
■ NVLink switch tray
72
Blackwell GPUs + 36 Grace CPUs
130 TB/s
total NVLink bandwidth
~13.4 TB
HBM3e in one rack (GB200)
~120 kW
per rack, liquid-cooled
Notes: SUPERCHIPS & NVL72 (6 min) GB200 superchip: one Grace CPU and two B200 GPUs on one board, linked by NVLink-C2C at 900 GB/s. The CPU's LPDDR5X memory (up to 480 GB) is accessible to the GPUs coherently – useful for large KV caches or embedding tables. GH200 was the Hopper version: one Grace + one H100/H200-class GPU. GB200 NVL72 rack: 18 compute trays (each with 2 GB200 superchips = 4 GPUs, 2 CPUs) and 9 NVLink Switch trays. Total 72 GPUs and 36 CPUs. Every GPU connects to every other at 1.8 TB/s through a copper NVLink "spine" at the back of the rack – about 130 TB/s total. The rack drawing shows the real layout: compute trays above and below the switch trays. Why it matters: for very large models, especially mixture-of-experts LLMs, splitting the model over 72 GPUs on NVLink is far faster than over 8-GPU nodes connected by networking. NVIDIA positions NVL72 for real-time inference of trillion-parameter models and for large-scale training. Trade-offs to stress for infrastructure people: • About 120–132 kW per rack (vs 10–20 kW for a typical enterprise rack). • Direct liquid cooling is required – coolant distribution units (CDUs), facility water loops. • Very heavy racks (well over 1,000 kg) – check floor loading. • It is bought and deployed as a complete rack-scale system, usually with vendor integration services. GB300 NVL72 is the Blackwell Ultra version with more memory per GPU; Vera Rubin NVL144 is announced as the next step.

## Slide 23: Data center vs workstation vs consumer GPUs
Why you should not build a production AI cluster from gaming cards
Capability | Data center (H100, L40S...) | Workstation (RTX PRO) | Consumer (GeForce RTX)
ECC memory | ✓ | ✓ | ✗ (mostly not)
Designed for 24/7 server airflow (passive) | ✓ | Mostly active, desktop | ✗
NVLink / NVSwitch | ✓ (top SKUs) | Limited | ✗
MIG partitioning | ✓ (A100, H100, B200...) | ✓ (RTX PRO Blackwell) | ✗
vGPU / virtualization support | ✓ | ✓ | ✗
Data center deployment allowed by driver EULA | ✓ | Desktop focus | ✗
Enterprise support and long life cycle | ✓ | ✓ | ✗
Price per GB of GPU memory | Highest | Medium | Lowest
Rule of thumb
Consumer: learning, hobby projects, personal experiments.
Workstation: developer desktops, design, local fine-tuning and demos.
Data center: anything shared, production, regulated or multi-tenant.
Notes: DATA CENTER vs WORKSTATION vs CONSUMER (4 min) A common question: "An RTX 5090 is much cheaper per TFLOP – why not fill racks with them?" Reasons: 1. Licensing: the GeForce driver licence terms do not permit data center deployment (with limited exceptions such as blockchain processing). This is a legal and compliance issue for enterprises. 2. Reliability: data center GPUs have ECC on memory, are validated for continuous operation, and are designed for server airflow. Consumer cards with large fans are not built for dense rack mounting. 3. Features: MIG, vGPU, NVLink/NVSwitch, confidential computing and enterprise management (DCGM features) are data center or professional features. 4. Memory: data center GPUs offer far more memory per GPU (80–288 GB HBM vs 16–32 GB GDDR7). 5. Support: enterprise support, long-term driver branches and multi-year availability. Workstation (RTX PRO) cards sit in the middle: professional drivers, ECC, large memory (RTX PRO 6000 Blackwell: 96 GB) and – new with Blackwell – MIG support. Excellent for developer desktops and departmental AI. Trainer tip: frame consumer GPUs positively – they are great for learning. Many attendees can practise CUDA and PyTorch on a laptop RTX GPU. Production belongs on data center GPUs.

## Slide 24: NVIDIA GPU infrastructure for AI workloads
03
How GPUs become an AI factory: compute, networking, storage, software, operations and facilities
Notes: MODULE 3 INTRO (1 min) Transition: "A GPU alone does nothing useful. In production, GPUs live inside servers, connected by several networks, fed by storage, scheduled by orchestration software, monitored by operations teams, and powered and cooled by facilities. NVIDIA calls the result an 'AI factory' – a data center whose output is intelligence (tokens)." Key message: an AI cluster is only as fast as its weakest layer. A cluster of the latest GPUs with a slow network or storage system will waste expensive GPU time.

## Slide 25: The AI factory: layers of a GPU infrastructure
Every layer must be sized together; the slowest layer limits the whole system
AI applications
Chatbots, copilots, RAG, agents, vision, recommendation
Product teams
AI software platform
NVIDIA AI Enterprise: NeMo, NIM, Triton, Dynamo, TensorRT-LLM, RAPIDS
ML platform team
Orchestration and scheduling
Kubernetes + GPU Operator, Slurm, Run:ai, Base Command Manager
Platform / DevOps
Storage
Parallel file systems, object storage, local NVMe, GPUDirect Storage
Infrastructure team
Networking
NVLink (scale-up), InfiniBand / Spectrum-X (scale-out), storage and management networks
Infrastructure team
Compute
DGX / HGX / MGX servers, GB200 NVL72 racks, cloud GPU instances
Infrastructure team
Facilities
Power, liquid or air cooling, floor space, rack density
Data center team
Notes: AI FACTORY LAYERS (5 min) Walk the layers bottom-up (the order a data center is built): 1. Facilities: power and cooling are now the first constraint for many AI projects. Lead times for power capacity can be longer than for GPUs. 2. Compute: GPU servers or rack-scale systems, on-premises or in the cloud. 3. Networking: at least four logical networks (detailed shortly). 4. Storage: must deliver training data fast enough and absorb checkpoints. 5. Orchestration: shares GPUs among users and teams – Kubernetes for cloud-native and inference, Slurm for traditional HPC-style training, often both. 6. AI software platform: frameworks, model-building and inference serving tools. 7. Applications: what the business actually uses. Right column: who typically owns each layer. Many projects struggle because these teams plan separately. Encourage a joint design – for example, the networking team needs to know the training topology, and the facilities team needs rack power figures before servers are ordered. Ask the room: "Which layer is the bottleneck in our organisation today?" – common answers are power/cooling, GPU availability, and data pipelines.

## Slide 26: Compute building blocks: DGX, HGX, MGX and cloud
Buy the complete system, a validated platform from an OEM, or rent capacity
NVIDIA DGX
NVIDIA's own integrated systems
DGX B200 / B300 (8 GPUs), DGX GB200 / GB300 racks
Full software stack and NVIDIA support
Reference designs: BasePOD and SuperPOD
Best for: Turnkey, fastest to deploy
NVIDIA HGX
GPU baseboard for OEM servers
4 or 8 SXM GPUs + NVSwitch on one board
Built into Dell, HPE, Lenovo, Supermicro and other servers
Same GPUs as DGX, vendor choice
Best for: Flexibility and existing vendor relationships
NVIDIA MGX
Modular server reference design
Mix CPUs (x86, Grace), GPUs and DPUs
PCIe GPU servers: L40S, H200 NVL, RTX PRO
Fits standard air-cooled racks
Best for: Mainstream enterprise and edge
Cloud GPU instances
Hyperscalers and GPU clouds
AWS, Azure, Google Cloud, OCI and specialist GPU clouds
On-demand, reserved or managed clusters
DGX Cloud on partner clouds
Best for: Elastic capacity, no capital expense
Notes: COMPUTE BUILDING BLOCKS (5 min) • DGX: NVIDIA-built systems (e.g. DGX B200: 8 B200 GPUs, 2 x86 CPUs, networking, storage). Comes with DGX OS, Base Command Manager and NVIDIA enterprise support. NVIDIA publishes reference architectures – DGX BasePOD (smaller clusters, partner storage) and DGX SuperPOD (large, validated designs of scalable units). • HGX: the GPU baseboard (8 SXM GPUs + NVSwitch) that server OEMs build into their own servers. Same GPU performance as DGX; you choose the vendor, CPUs, memory, NICs and support model. This is the most common way enterprises and clouds buy 8-GPU servers. • MGX: a modular reference architecture that lets OEMs build many server types (1U to 4U, x86 or Grace, air or liquid cooled) from common parts. This is where PCIe GPU servers for enterprise AI, such as "RTX PRO servers" and L40S/H200 NVL systems, often come from. • Cloud: all major clouds offer H100/H200/B200 and GB200 instances, plus L4/L40S for inference. Specialist GPU clouds also offer large clusters. NVIDIA DGX Cloud runs on partner clouds. Discussion: on-prem vs cloud is covered on a later slide. For now emphasise that the GPU silicon is the same; what differs is integration effort, support model, flexibility and cost model (CapEx vs OpEx).

## Slide 27: Anatomy of an 8-GPU AI server (HGX / DGX class)
Balanced design: every GPU gets its own path to the network and fast access to its peers
GPU 0
GPU 1
GPU 2
GPU 3
NVSwitch: all-to-all NVLink, 1.8 TB/s per GPU (Blackwell)
GPU 4
GPU 5
GPU 6
GPU 7
PCIe Gen5 switches: link GPUs to NICs, NVMe and CPUs
CPU 0
x86 or Grace
CPU 1
2–4 TB RAM
8× ConnectX
400 Gb/s each
2× BlueField-3
DPU
NVMe SSDs: OS + local data cache
BMC: out-of-band management
Example: DGX B200
8×
B200 GPUs
1,440 GB
total HBM3e
72 PF
FP8 training
144 PF
FP4 inference
~14.3 kW
maximum power
1:1
GPU-to-NIC ratio
PF = petaFLOPS. FP4 figure is with sparsity, per NVIDIA's datasheet.
Notes: 8-GPU SERVER ANATOMY (6 min) This is the standard building block of most AI clusters. Top half – the GPU complex: 8 SXM GPUs on an HGX baseboard, fully connected through NVSwitch. Inside the box, GPU-to-GPU traffic never touches PCIe or the CPU. Middle – PCIe switches: each GPU is paired with a network adapter (NIC) under the same PCIe switch. With GPUDirect RDMA, a GPU sends data straight to its NIC and across the network without copying through CPU memory. Bottom: • 2 CPUs (Intel Xeon, AMD EPYC, or Grace in Grace-based systems) with 2–4 TB of RAM. They run the OS, data loading, preprocessing and orchestration agents. • 8 ConnectX-7 (400 Gb/s) or ConnectX-8 SuperNICs (800 Gb/s on Blackwell Ultra platforms) – one per GPU – for the compute (east-west) fabric. This 1:1 GPU-to-NIC ratio is a key design principle for training clusters. • 2 BlueField-3 DPUs for the storage and in-band management network; they can also offload security and storage services. • NVMe SSDs for the OS and a fast local cache for datasets and checkpoints. • BMC for out-of-band management (power cycling, firmware, sensors). DGX B200 figures (from the datasheet): 8 B200 GPUs, 1,440 GB HBM3e total, 72 PFLOPS FP8 training, 144 PFLOPS FP4 inference (with sparsity), about 14.3 kW maximum power. Note: one server now draws more power than an entire typical enterprise rack.

## Slide 28: Networking: four distinct networks in an AI cluster
Separate fabrics keep GPU traffic, storage traffic and management traffic from interfering
Network
Technology
Typical bandwidth
Scale-up (NVLink)
GPU ↔ GPU inside a node or NVL72 rack
NVLink + NVSwitch
0.9–1.8 TB/s per GPU
Scale-out compute fabric
East-west traffic between nodes for collective operations
InfiniBand Quantum-2 / X800 or Spectrum-X Ethernet (RoCE)
400–800 Gb/s per GPU
Storage / front-end
Dataset reads, checkpoints, user and service access
Ethernet via BlueField-3 DPUs
100–400 Gb/s per node
Management (in-band + OOB)
Provisioning, monitoring, BMC access
1–25 GbE Ethernet
Low bandwidth, high availability
Key technologies: GPUDirect RDMA (GPU ↔ NIC with no CPU copy) · SHARP in-network reduction · adaptive routing · congestion control
Notes: FOUR NETWORKS (6 min) 1. Scale-up – NVLink/NVSwitch inside a node (8 GPUs) or a rack (NVL72). Highest bandwidth, lowest latency. Used for tensor parallelism and expert parallelism. 2. Scale-out compute fabric – the "east-west" or "backend" network connecting GPUs in different nodes. Carries all-reduce/all-gather traffic for data parallelism and pipeline parallelism. Two NVIDIA options: • InfiniBand (Quantum-2 NDR 400 Gb/s; Quantum-X800 at 800 Gb/s) – lossless, very low latency, SHARP in-network computing, the traditional choice for the largest training clusters. • Spectrum-X Ethernet (Spectrum-4 switches + SuperNICs) – Ethernet with RoCE, adaptive routing and congestion control tuned for AI. Attractive for organisations standardised on Ethernet. Design rules: one NIC per GPU, non-blocking (1:1) fat-tree or rail-optimized topology, and identical cable lengths and firmware. 3. Storage / front-end network – connects nodes to shared storage and to users/services. Often 2 × 200–400 Gb/s per node via BlueField-3 DPUs. Kept separate so checkpoint bursts don't slow down GPU collectives. 4. Management – in-band (OS provisioning, monitoring agents, Kubernetes control plane) and out-of-band (BMC/IPMI/Redfish). Low bandwidth but must be highly available. Bottom callout: • GPUDirect RDMA – NIC reads/writes GPU memory directly. • SHARP – switches perform reduction maths inside the network, cutting all-reduce traffic. • Adaptive routing and congestion control – spread flows across paths, avoid hotspots. Warning: networking is often 10–20% of AI cluster cost but can decide whether expensive GPUs sit idle waiting for communication.

## Slide 29: Rail-optimized topology and scaling to a SuperPOD
GPU n in every node connects to the same leaf switch ("rail"), so most traffic is one hop away
Spine 0
Spine 1
Spine 2
Spine 3
Rail 0
Rail 1
Rail 2
Rail 3
Rail 4
Rail 5
Rail 6
Rail 7
Node 0
GPU0 … GPU7
Node 1
GPU0 … GPU7
Node 2
GPU0 … GPU7
Node 3
GPU0 … GPU7
Leaf layer
Spine layer
Scaling with scalable units (SU)
Rail-optimized: NIC n of every node goes to rail switch n; same-rank GPUs are one hop apart.
Scalable unit: a DGX H100/B200 SuperPOD SU is 32 nodes = 256 GPUs with its own leaf switches.
Spine layer joins multiple SUs into clusters of thousands of GPUs, non-blocking.
GB200 SuperPOD is built from NVL72 racks, e.g. 8 racks = 576 GPUs.
Notes: RAIL-OPTIMIZED TOPOLOGY (5 min) Explain the diagram: each node has 8 GPUs and 8 NICs. NIC 0 of every node connects to leaf switch "Rail 0", NIC 1 to "Rail 1", and so on. The leaf switches then connect to every spine switch. Why: in data-parallel and pipeline-parallel training, GPU n in one node mostly talks to GPU n in the other nodes (same rank in each NVLink group). With rail-optimized wiring that traffic stays within one leaf switch – one hop, lowest latency. Cross-rail traffic can first move over NVLink inside the node, then go out on the right rail (NCCL handles this automatically, called "PXN"). Scalable unit (SU): NVIDIA's DGX SuperPOD reference architecture builds clusters from SUs. For DGX H100/B200 SuperPODs an SU is 32 nodes (256 GPUs) with its own set of rail leaf switches. Multiple SUs connect through a spine layer (and a core layer for very large clusters) to reach thousands of GPUs while staying non-blocking. GB200-based SuperPODs are built from NVL72 racks: each rack is its own 72-GPU NVLink domain, and racks connect over the InfiniBand or Spectrum-X scale-out fabric (8 racks = 576 GPUs per unit in NVIDIA's reference design). Practical point: cabling is a major project – thousands of optical cables and transceivers. Validate with cable testers, then NCCL tests (all_reduce_perf) before handing the cluster to users.

## Slide 30: Storage and the data pipeline
Keep GPUs busy: data must arrive faster than the GPUs can consume it
Data lake / object store
Raw data, models, archives
High-performance file system
Parallel FS: Lustre, GPFS, WEKA, VAST, DDN...
Node-local NVMe cache
Hot datasets, staged shards
GPUDirect Storage
NVMe / network → GPU, CPU bypassed
GPU memory (HBM)
Training batches, model weights
Checkpoints flow back down the same path, in large bursts
Read throughput
Vision and multimodal training can need many GB/s per node. Size storage bandwidth to the GPU count, not only to capacity.
Checkpoint bursts
Large models write checkpoints of hundreds of GB to TBs. Fast writes shorten pauses and protect against failures.
Metadata and small files
Millions of small files overload metadata servers. Pack data into shards (WebDataset, TFRecord, Parquet).
Notes: STORAGE (5 min) Walk the pipeline left to right: • Data lake/object storage (S3-compatible) holds raw data, curated datasets, model artifacts – cheap and huge. • High-performance parallel file system (Lustre, IBM Storage Scale/GPFS, WEKA, VAST, DDN, NetApp, Pure and others, many certified for DGX SuperPOD) delivers aggregate bandwidth to all nodes. • Local NVMe on each node caches hot data and can stage checkpoints. • GPUDirect Storage (GDS, part of Magnum IO) lets data move from NVMe or network storage directly into GPU memory using DMA, without bouncing through CPU memory. This reduces CPU load and latency. The three requirements: 1. Read throughput: training jobs read data continuously. A rule of thumb in NVIDIA reference architectures is to plan for multiple GB/s per node for vision/multimodal workloads; LLM text training needs less read bandwidth but more checkpoint bandwidth. 2. Checkpoints: a 70B model with optimizer state is over 1 TB. Synchronous checkpoints pause training; faster storage or asynchronous/tiered checkpointing (to local NVMe first) reduces lost GPU time. Frequent checkpointing matters because at scale hardware failures happen daily. 3. Metadata: millions of small JPEGs or text files overwhelm metadata servers – pack them into larger shards. For inference: storage matters for model loading (cold start of a 140 GB model) and RAG vector databases. Fast model loading improves autoscaling.

## Slide 31: Software stack and orchestration
Two common paths, Kubernetes and Slurm, on the same GPU foundation
NVIDIA AI Enterprise: NeMo · NIM · Triton · Dynamo · TensorRT-LLM · RAPIDS · NGC containers
Kubernetes path (cloud-native)
GPU Operator: installs driver, container toolkit, device plugin, DCGM exporter, MIG manager
Network Operator: RDMA / GPUDirect for InfiniBand and RoCE
Schedulers: Run:ai, Kueue, Volcano for queues and quotas
Best for: inference services, MLOps pipelines, multi-tenant platforms
Slurm path (HPC-style)
Slurm: batch scheduler with gang scheduling, topology-aware placement
Pyxis + Enroot: run NGC containers as unprivileged Slurm jobs
Base Command Manager: provisioning and cluster management
Best for: large multi-node training and research clusters
Node foundation: Linux OS · NVIDIA driver · Fabric Manager (NVSwitch) · NVIDIA Container Toolkit · DCGM · MOFED / DOCA networking
Notes: SOFTWARE & ORCHESTRATION (6 min) Bottom layer – every GPU node needs: a supported Linux OS, the NVIDIA driver, Fabric Manager (on NVSwitch systems), the NVIDIA Container Toolkit (so containers can access GPUs), DCGM for health, and networking drivers (MOFED/DOCA) for InfiniBand/RoCE. Kubernetes path: • The NVIDIA GPU Operator automates the GPU software lifecycle on Kubernetes: driver containers, container toolkit, the device plugin (which advertises nvidia.com/gpu resources to the scheduler), GPU Feature Discovery (node labels like GPU model and memory), DCGM Exporter (Prometheus metrics), MIG Manager and validation. • The Network Operator does the same for RDMA networking. • Default Kubernetes scheduling is not GPU-aware enough for training (no gang scheduling, quotas or fair share), so teams add Run:ai (acquired by NVIDIA), Kueue or Volcano. • Strong for inference (NIM, Triton, KServe), MLOps pipelines and multi-tenant platforms. Slurm path: • The traditional HPC scheduler; excellent for large multi-node training with gang scheduling (all GPUs start together) and topology-aware placement. • Pyxis (a Slurm plugin) + Enroot run NGC containers without root. • NVIDIA Base Command Manager provisions and manages clusters (both Slurm and Kubernetes). Top layer – NVIDIA AI Enterprise: the supported software suite – NeMo for building and customizing models, NIM for optimized inference microservices, Triton and Dynamo for serving, TensorRT-LLM for optimized LLM engines, RAPIDS for data science. Many organizations run both: Slurm for big training, Kubernetes for inference and services.

## Slide 32: GPU sharing strategies
Most workloads don't need a whole GPU; sharing raises utilization, but isolation differs
MIG
Multi-Instance GPU
Hardware partitions, up to 7 per GPU, each with dedicated SMs, L2 and memory
Isolation: Strong (hardware)
Use for: Multi-tenant inference, notebooks, guaranteed QoS
Time-slicing
Oversubscription
Workloads take turns on the whole GPU; memory is shared
Isolation: None
Use for: Dev and test, bursty light jobs
MPS
Multi-Process Service
Kernels from several processes run at the same time on the SMs
Isolation: Limited
Use for: Many small inference processes on one GPU
VM
VM
VM
VM
vGPU
NVIDIA virtual GPU
Hypervisor shares the GPU across VMs (licensed)
Isolation: VM-level
Use for: VDI, virtualized enterprise apps, AI in VMs
Notes: GPU SHARING (6 min) GPUs are expensive; many inference services, notebooks and dev jobs use only a fraction of a GPU. Four ways to share: 1. MIG (Multi-Instance GPU) – A100, H100, H200, B200 and later (and RTX PRO Blackwell). The GPU is split in hardware into up to 7 instances, each with dedicated SMs, L2 cache slices, memory controllers and memory. Example H100 80 GB profiles: 1g.10gb (7 instances), 2g.20gb, 3g.40gb, 7g.80gb. Strong isolation and guaranteed performance – a noisy neighbour cannot slow you down. Downsides: fixed profile sizes, and reconfiguration requires the GPU to be idle. In Kubernetes, the GPU Operator's MIG Manager applies profiles; pods request e.g. nvidia.com/mig-1g.10gb. 2. Time-slicing – the device plugin advertises one GPU as N "replicas"; workloads take turns. Simple and works on any GPU, but there is no memory isolation (one job can use all memory and crash others) and no performance guarantee. Good for dev/test. 3. MPS (Multi-Process Service) – lets kernels from multiple processes run concurrently on the SMs, improving utilization for many small inference processes. Limited isolation; can set per-client SM and memory limits. Can be combined with MIG. 4. vGPU – NVIDIA's virtualization software (licensed) for VMware, Nutanix, Red Hat and others. Splits a GPU across VMs with time-sliced or MIG-backed profiles. Standard for VDI and virtualized enterprise environments. Decision guide: production multi-tenant → MIG; dev → time-slicing; many tiny processes → MPS; VMs → vGPU.

## Slide 33: Mapping AI workloads to infrastructure
Training, fine-tuning and inference stress different parts of the stack
Workload | GPUs | Interconnect / network | Storage | Orchestration
Pre-training | Hundreds to thousands; HGX B200 / NVL72 | NVLink + non-blocking IB / Spectrum-X, 1 NIC per GPU | Parallel FS, fast checkpoints | Slurm or K8s + gang scheduling
Full fine-tuning | 8–64 GPUs (HGX H100 / H200) | NVSwitch in node; IB/RoCE across nodes | Shared FS, checkpoints | Slurm, Run:ai, Kubeflow
LoRA / PEFT | 1–8 GPUs (L40S, H100, RTX PRO) | PCIe or NVLink; standard Ethernet | Modest; model + dataset | K8s jobs, notebooks
Real-time LLM inference | 1–8 GPUs per replica; H200 / B200 / L40S | NVLink for tensor parallel; front-end Ethernet | Fast model loading | K8s + NIM / Triton / Dynamo, autoscaling
Batch inference / embeddings | Many small GPUs or MIG slices (L4, L40S) | Standard Ethernet | Object storage throughput | K8s batch, queues
RAG applications | Inference GPUs + embedding GPUs | Front-end Ethernet | Vector DB on fast storage | K8s microservices
Notes: WORKLOAD MAPPING (5 min) Use this table as a reference card – the class does not need to memorise it. Emphasise the contrasts: • Pre-training is a "tightly coupled" workload: every step synchronises all GPUs, so one slow link or failed GPU slows or stops everything. Needs the best interconnect and network, gang scheduling, fast checkpointing and automatic job restart. • Full fine-tuning is the same pattern at smaller scale – typically 1–8 nodes. • LoRA/PEFT fits on a few GPUs and tolerates standard networking – ideal for enterprise teams adapting open models on their own data. • Real-time inference is latency-sensitive and "loosely coupled": many independent replicas behind a load balancer, each replica using 1–8 GPUs. Key concerns: tokens/s, time-to-first-token, autoscaling, cold start (model loading speed). Serving engines (TensorRT-LLM, vLLM via NIM, Triton, Dynamo) use continuous batching and paged KV cache to raise throughput. Dynamo adds disaggregated serving – separating the prefill and decode phases onto different GPUs. • Batch inference/embeddings: throughput-oriented; can use cheaper GPUs or MIG slices, and spot/preemptible capacity in the cloud. • RAG: a system of services – embedding model, vector database, reranker and LLM – each sized separately. Key message: many enterprises over-buy training infrastructure when most of their demand will be inference. Size for the workload mix.

## Slide 34: Sizing GPU memory for an LLM: worked example
Model: a 70-billion-parameter LLM (Llama 3 70B class: 80 layers, 8 KV heads, head size 128)
Inference
Weights = parameters × bytes per parameter
70B × 2 bytes (BF16) = 140 GB · FP8 = 70 GB · FP4 ≈ 35 GB
KV cache per token = 2 × layers × KV heads × head size × bytes
2 × 80 × 8 × 128 × 2 B ≈ 0.33 MB per token (FP16)
32 users × 8K tokens ≈ 262K tokens ≈ 86 GB
FP8 weights + KV cache ≈ 156 GB plus ~10% overhead
→ 2× H100 80 GB (tensor parallel) or 1× B200
Training
Full fine-tune, mixed precision + Adam ≈ 16 bytes per parameter
weights 2 + gradients 2 + FP32 master 4 + Adam states 8
70B × 16 B ≈ 1.12 TB, plus activations
Shard with FSDP / ZeRO-3 across GPUs
1.12 TB ÷ 80 GB ≈ 14 GPUs minimum, so in practice 16–32 H100 (2–4 nodes)
QLoRA (4-bit base + adapters)
~35 GB weights + adapters and activations
→ QLoRA fits on 1× 80 GB GPU (H100) or 1× RTX PRO 6000
Notes: SIZING WORKED EXAMPLE (8 min) – the most practical slide of the module; go slowly and write on the whiteboard. INFERENCE 1. Weights: parameters × bytes/parameter. 70B × 2 bytes (BF16) = 140 GB. Quantized to FP8: 70 GB. FP4/INT4: about 35 GB. 2. KV cache: for every token in every active conversation, the model stores a key and a value vector per layer. Formula: 2 (K and V) × layers × KV heads × head dimension × bytes per value. For Llama-3-70B: 2 × 80 × 8 × 128 × 2 bytes = 327,680 bytes ≈ 0.33 MB per token. (Grouped-query attention with only 8 KV heads keeps this small; older models without GQA need about 8x more.) 3. Concurrency: 32 users each with an 8K-token context = 262,144 tokens × 0.33 MB ≈ 86 GB. 4. Total: 70 GB (FP8 weights) + 86 GB (KV) ≈ 156 GB, plus runtime overhead → 2× H100 80 GB using tensor parallelism, or a single B200 (180 GB). An H200 (141 GB) would need fewer concurrent users or an FP8 KV cache. Point out: the KV cache can be bigger than the model! Long context and many users drive memory needs. Techniques to reduce it: FP8 KV cache, paged attention, KV offload to CPU memory (helped by NVLink-C2C on Grace systems). TRAINING Mixed precision with the Adam optimizer needs about 16 bytes per parameter: BF16 weights (2) + BF16 gradients (2) + FP32 master weights (4) + Adam first and second moments in FP32 (8). 70B × 16 = 1.12 TB before activations. Sharded across GPUs with FSDP or DeepSpeed ZeRO-3, that needs at least 14 × 80 GB, in practice 16–32 GPUs to leave room for activations and a reasonable batch size. QLoRA: base model frozen in 4-bit (~35 GB), train small adapters → fits on a single 80 GB GPU. Exercise: ask participants to size an 8B model for 100 users at 4K context (8B FP16 = 16 GB; KV for Llama-3-8B ≈ 0.125 MB/token × 409,600 tokens ≈ 51 GB → 1× H100 80 GB, or L40S 48 GB with FP8 weights and FP8 KV cache).

## Slide 35: Monitoring and operating GPU infrastructure
Watch utilization, health and errors: idle or throttled GPUs are expensive
Utilization
GPU util %, SM activity, Tensor Core activity
Memory
Framebuffer used, memory bandwidth utilization
Power and thermals
Watts vs limit, temperature, clock throttle reasons
XID errors
Driver-reported faults: memory, NVLink, falling off the bus
ECC and row remapping
Correctable / uncorrectable errors, pending remaps
Interconnect
NVLink and PCIe throughput, replay and CRC errors
Everyday commands
# GPU status, memory, processes
nvidia-smi
# Topology: NVLink vs PCIe paths
nvidia-smi topo -m
# Details: ECC, remapped rows, clocks
nvidia-smi -q -d ECC,ROW_REMAPPER
# List MIG GPU instance profiles
nvidia-smi mig -lgip
# Health diagnostics (level 3)
dcgmi diag -r 3
# GPUs visible to Kubernetes
kubectl describe node | grep nvidia.com
Notes: MONITORING & OPERATIONS (6 min) Left – the metrics that matter (exported by DCGM Exporter to Prometheus/Grafana in Kubernetes, or collected by DCGM on Slurm clusters): • Utilization: careful – "GPU utilization %" in nvidia-smi only means "a kernel was running", not how busy the SMs were. Use DCGM profiling metrics: SM activity (DCGM_FI_PROF_SM_ACTIVE) and Tensor Core activity (DCGM_FI_PROF_PIPE_TENSOR_ACTIVE) for real efficiency. • Memory: framebuffer used vs total (OOM risk), and memory bandwidth utilization (DRAM active). • Power and thermals: power draw vs limit and clock throttle reasons (thermal, power cap, HW slowdown). Throttled GPUs silently slow the whole training job. • XID errors: error codes in the kernel log (dmesg) from the NVIDIA driver. Examples: XID 79 = GPU has fallen off the bus (hardware/PCIe issue); XID 48/63/64/94/95 relate to ECC/memory faults; XID 74 = NVLink error. Build alerting and runbooks for common XIDs. • ECC and row remapping: rising uncorrectable errors or a pending row remap means the GPU needs a reset or RMA. • Interconnect: NVLink/PCIe errors and throughput; InfiniBand port counters for the fabric. Right – commands to demonstrate live if you have a GPU system: • nvidia-smi – quick status. • nvidia-smi topo -m – shows how GPUs and NICs connect (NV18 = 18 NVLinks; PIX/PXB = same PCIe switch; SYS = crosses CPU sockets). • nvidia-smi -q -d ECC,ROW_REMAPPER – memory health. • nvidia-smi mig -lgip – available MIG profiles. • dcgmi diag -r 3 – extended health test (run before putting a node into production and after repairs). • kubectl describe node – check that nvidia.com/gpu resources are advertised. Operational practice: automated health checks before each job (pre-flight), drain and repair nodes that fail, and track GPU-hours used vs available as a business KPI.

## Slide 36: Command reference: GPUs, SMs, cores, DPUs and NPUs
Node-level commands to see what hardware is installed and how hard it is working
GPU nvidia-smi -L
Lists every GPU the driver can see, with model name and UUID. First check after an install or when a GPU seems missing.
GPU nvidia-smi -q -d MEMORY,CLOCK,POWER
Per-GPU detail: memory used vs total, SM and memory clocks, power draw vs limit. Leave out the filter for the full report.
SM / CUDA CORES deviceQuery
CUDA sample that prints SM count and CUDA cores per SM, e.g. H100 SXM: 132 SMs × 128 = 16,896 CUDA cores.
CUDA nvcc --version
Shows the installed CUDA toolkit version. The nvidia-smi header shows the newest CUDA version the driver supports.
TENSOR nvidia-smi --query-gpu=compute_cap --format=csv
Compute capability gives the Tensor Core generation: 8.0 Ampere (3rd), 9.0 Hopper (4th), 10.0 Blackwell (5th).
SM / TENSOR dcgmi dmon -e 1002,1003,1004
Live SM activity, SM occupancy and Tensor Core activity per GPU. Low Tensor activity on an AI job points to FP32 or data stalls.
PROFILING ncu --set full ./app
Nsight Compute profiles each CUDA kernel: SM throughput, Tensor Core use, memory bandwidth and what limits occupancy.
DPU lspci | grep -i bluefield
Confirms the BlueField DPU is on the PCIe bus and shows its PCI address and model.
DPU mst start && mst status -v
NVIDIA Firmware Tools: maps each DPU or NIC to its /dev/mst device, PCI address and network interface.
DPU mlxconfig -d <dev> q INTERNAL_CPU_MODEL
Shows whether the BlueField runs in DPU mode (its Arm cores own the NIC) or as a plain NIC.
NPU npu-smi info
Huawei Ascend NPUs: the nvidia-smi equivalent, listing each NPU with health, power, temperature and AI Core usage.
NPU xrt-smi examine
AMD Ryzen AI (XDNA) NPUs: shows the device, firmware version and active contexts.
CUDA cores = SMs × cores per SM; Tensor Cores = 4 per SM since Ampere (H100 SXM: 528). NPUs are not NVIDIA products, so their tools are vendor-specific.
Notes: MONITORING & OPERATIONS (6 min) Left – the metrics that matter (exported by DCGM Exporter to Prometheus/Grafana in Kubernetes, or collected by DCGM on Slurm clusters): • Utilization: careful – "GPU utilization %" in nvidia-smi only means "a kernel was running", not how busy the SMs were. Use DCGM profiling metrics: SM activity (DCGM_FI_PROF_SM_ACTIVE) and Tensor Core activity (DCGM_FI_PROF_PIPE_TENSOR_ACTIVE) for real efficiency. • Memory: framebuffer used vs total (OOM risk), and memory bandwidth utilization (DRAM active). • Power and thermals: power draw vs limit and clock throttle reasons (thermal, power cap, HW slowdown). Throttled GPUs silently slow the whole training job. • XID errors: error codes in the kernel log (dmesg) from the NVIDIA driver. Examples: XID 79 = GPU has fallen off the bus (hardware/PCIe issue); XID 48/63/64/94/95 relate to ECC/memory faults; XID 74 = NVLink error. Build alerting and runbooks for common XIDs. • ECC and row remapping: rising uncorrectable errors or a pending row remap means the GPU needs a reset or RMA. • Interconnect: NVLink/PCIe errors and throughput; InfiniBand port counters for the fabric. Right – commands to demonstrate live if you have a GPU system: • nvidia-smi – quick status. • nvidia-smi topo -m – shows how GPUs and NICs connect (NV18 = 18 NVLinks; PIX/PXB = same PCIe switch; SYS = crosses CPU sockets). • nvidia-smi -q -d ECC,ROW_REMAPPER – memory health. • nvidia-smi mig -lgip – available MIG profiles. • dcgmi diag -r 3 – extended health test (run before putting a node into production and after repairs). • kubectl describe node – check that nvidia.com/gpu resources are advertised. Operational practice: automated health checks before each job (pre-flight), drain and repair nodes that fail, and track GPU-hours used vs available as a business KPI.

## Slide 37: Command reference: monitoring GPUs in Kubernetes
Confirm GPUs are discovered, healthy, allocated to pods and actually busy
Area | Command | What it tells you
Nodes | kubectl get nodes -L nvidia.com/gpu.product,nvidia.com/gpu.count | GPU model and count per node, from GPU Feature Discovery labels. Blank columns mean no GPUs were discovered.
 | kubectl get nodes -L nvidia.com/mig.config.state | MIG reconfiguration state per node: success, pending or failed.
GPU Operator | kubectl get clusterpolicies.nvidia.com | Overall GPU Operator status; "ready" means driver, toolkit and plugins are healthy on every GPU node.
 | kubectl get pods -n gpu-operator -o wide | Driver, toolkit, device plugin, DCGM exporter and MIG manager pods per node; all should be Running.
 | kubectl logs -n gpu-operator ds/nvidia-device-plugin-daemonset | GPU registration with the kubelet, and GPUs marked unhealthy after XID errors.
Workloads | kubectl exec -it <pod> -- nvidia-smi | Shows which GPU the pod received, with live utilization and memory, from inside the container.
 | kubectl get events -A --field-selector reason=FailedScheduling | Pods stuck Pending; "Insufficient nvidia.com/gpu" means no free GPU matches the request.
 | kubectl top pod -A | CPU and memory only: metrics-server does not report GPUs, so use DCGM metrics for GPU usage.
Metrics | kubectl port-forward -n gpu-operator svc/nvidia-dcgm-exporter 9400 | Then curl localhost:9400/metrics for raw per-GPU metrics labelled by pod: utilization, memory, power, XID.
 | avg by (pod) (DCGM_FI_PROF_PIPE_TENSOR_ACTIVE) | PromQL for Prometheus or Grafana: Tensor Core activity per pod, the clearest sign an AI job uses the GPU well.
Assumes the NVIDIA GPU Operator installed in the gpu-operator namespace with default names; 9400 is the DCGM exporter's default port.
Notes: MONITORING & OPERATIONS (6 min) Left – the metrics that matter (exported by DCGM Exporter to Prometheus/Grafana in Kubernetes, or collected by DCGM on Slurm clusters): • Utilization: careful – "GPU utilization %" in nvidia-smi only means "a kernel was running", not how busy the SMs were. Use DCGM profiling metrics: SM activity (DCGM_FI_PROF_SM_ACTIVE) and Tensor Core activity (DCGM_FI_PROF_PIPE_TENSOR_ACTIVE) for real efficiency. • Memory: framebuffer used vs total (OOM risk), and memory bandwidth utilization (DRAM active). • Power and thermals: power draw vs limit and clock throttle reasons (thermal, power cap, HW slowdown). Throttled GPUs silently slow the whole training job. • XID errors: error codes in the kernel log (dmesg) from the NVIDIA driver. Examples: XID 79 = GPU has fallen off the bus (hardware/PCIe issue); XID 48/63/64/94/95 relate to ECC/memory faults; XID 74 = NVLink error. Build alerting and runbooks for common XIDs. • ECC and row remapping: rising uncorrectable errors or a pending row remap means the GPU needs a reset or RMA. • Interconnect: NVLink/PCIe errors and throughput; InfiniBand port counters for the fabric. Right – commands to demonstrate live if you have a GPU system: • nvidia-smi – quick status. • nvidia-smi topo -m – shows how GPUs and NICs connect (NV18 = 18 NVLinks; PIX/PXB = same PCIe switch; SYS = crosses CPU sockets). • nvidia-smi -q -d ECC,ROW_REMAPPER – memory health. • nvidia-smi mig -lgip – available MIG profiles. • dcgmi diag -r 3 – extended health test (run before putting a node into production and after repairs). • kubectl describe node – check that nvidia.com/gpu resources are advertised. Operational practice: automated health checks before each job (pre-flight), drain and repair nodes that fail, and track GPU-hours used vs available as a business KPI.

## Slide 38: Power, cooling and facility planning
AI racks draw many times the power of traditional enterprise racks
Chart: Approximate power per rack (kW)
| Typical enterprise rack | 4× HGX H100 servers | 4× DGX B200 | GB200 NVL72
kW per rack | 10 | 41 | 57 | 120
Estimates from published maximum system power (~10.2 kW HGX H100, ~14.3 kW DGX B200), excluding networking.
Cooling options
Air: practical up to ~30–40 kW per rack with hot-aisle containment.
Direct liquid cooling: cold plates on GPUs and CPUs; needed for NVL72-class racks.
Planning checklist
Power per rack and redundancy (N+1, 2N)
Floor loading: liquid-cooled racks exceed 1,000 kg
Lead time for power and cooling upgrades
PUE and sustainability targets
Notes: POWER & COOLING (5 min) The chart compares approximate rack power: • A typical enterprise rack is designed for about 5–15 kW. • Four HGX H100 servers (about 10.2 kW each) ≈ 41 kW – already beyond many existing data halls, which is why many sites put only 1–2 GPU servers per rack. • Four DGX B200 (about 14.3 kW each) ≈ 57 kW. • A GB200 NVL72 rack ≈ 120–132 kW, liquid-cooled. (Networking switches add more.) Cooling: • Air cooling with hot/cold aisle containment and rear-door heat exchangers works up to roughly 30–40 kW per rack. • Direct-to-chip liquid cooling uses cold plates on GPUs/CPUs with coolant distribution units (CDUs) connected to facility water. It removes most of the heat with liquid, which is much more efficient than air, and enables 100 kW+ racks. Some designs use warm-water cooling, which allows heat reuse and lowers PUE. Planning checklist: • Power capacity and redundancy – utility upgrades can take 12–36 months. • Floor loading and rack weight. • Electrical design for fast, large swings in GPU power draw during training. • Sustainability: PUE, renewable energy, heat reuse. Message for leadership: GPU procurement and facility readiness must be planned together – many organizations have received GPUs they could not power. Colocation providers offering high-density, liquid-cooled space and cloud GPUs are alternatives while facilities are upgraded.

## Slide 39: Deployment models: on-premises, cloud and hybrid
Most enterprises end up hybrid: steady base load on-premises, bursts and experiments in the cloud
On-premises / colocation
Pros: lowest cost at high utilization, data control, predictable performance
Cons: capital expense, facility work, long lead times, refresh risk
Fits: steady, high-utilization training and inference, regulated data
Public cloud and GPU clouds
Pros: fast start, elastic, latest GPUs, managed services
Cons: expensive at constant high use, capacity limits, data egress
Fits: experiments, bursty training, early-stage projects
Hybrid
Pros: base load on-prem, burst to cloud, avoids lock-in
Cons: needs consistent tooling, identity and data movement
Fits: most enterprises; Kubernetes and NGC containers help portability
Decision drivers: expected GPU utilization, data sensitivity and location, time to value, in-house skills and total cost over 3–5 years.
Notes: DEPLOYMENT MODELS (4 min) On-premises (or colocation): best total cost when GPUs are busy most of the time (a common rule of thumb is that above roughly 60–70% sustained utilization, owning becomes cheaper than renting over 3 years, but run your own TCO). Full control of data and performance. Requires capital, facility readiness, skilled staff and a refresh plan as new generations arrive yearly. Cloud: instant access to the newest GPUs without facility work; pay as you go; managed Kubernetes, managed Slurm and model services. Costs grow quickly at constant high utilization; large GPU clusters may require reservations; moving large datasets out of the cloud has egress costs. Hybrid: the most common enterprise pattern. Keep a steady base of on-prem GPUs for predictable workloads and sensitive data; use cloud for bursts, experiments and access to new GPU types. Make it work with portable tooling: containers from NGC, Kubernetes with the GPU Operator in both places, consistent identity and MLOps pipelines. Discussion question: "Which model fits our organisation today, and what would change that answer?"

## Slide 40: Key takeaways
Six ideas to remember
01
Compute, memory, interconnect
AI performance is a balance of all three; find the bottleneck first.
02
Tensor Cores + low precision
Each format step (BF16 → FP8 → FP4) roughly doubles throughput.
03
Memory decides inference
HBM capacity and bandwidth set model size, batch size and tokens per second.
04
Pick GPUs by workload
Training flagships, universal PCIe GPUs and edge modules each have a place.
05
The cluster is the computer
NVLink, a rail-optimized fabric, storage and orchestration matter as much as GPUs.
06
Plan power and operations early
Facilities, monitoring and sharing (MIG) decide real-world value.
Notes: KEY TAKEAWAYS (3 min) Summarize by tying back to the three modules: 1. Every GPU discussion comes back to compute, memory and interconnect – diagnose the bottleneck before buying or tuning. 2. Tensor Cores and lower-precision formats are the main source of AI speed-ups across generations. 3. For inference especially, memory capacity and bandwidth matter more than peak TFLOPS. 4. There is no single "best GPU" – match the class to the workload and budget. 5. At scale, the cluster (NVLink domains, network fabric, storage, scheduler) is the computer. 6. Power, cooling, monitoring and sharing strategy decide whether expensive GPUs actually deliver value. Revisit the questions collected on the flip chart at the start and check that each one has been answered.

## Slide 41: Knowledge check
Discuss in pairs for 5 minutes, then we review together
Q1
What is the difference between a CUDA core and a Tensor Core, and which one does most of the work in LLM training?
Q2
Why can an H200 serve LLMs much faster than an H100 even though their compute is the same?
Q3
Decode the product name "GB200 NVL72". What does each part mean?
Q4
A team needs to fine-tune a 70B model with QLoRA. Which GPU class would you recommend, and why?
Q5
Name the four networks in an AI cluster and the main purpose of each.
Q6
Your Kubernetes cluster must give 7 teams isolated, guaranteed GPU slices for inference. Which sharing method fits?
Notes: KNOWLEDGE CHECK – ANSWER KEY (10 min) Q1. CUDA cores do one scalar operation per clock (general-purpose maths); Tensor Cores do a whole small matrix multiply-accumulate per instruction. Tensor Cores do most of the work in LLM training (the matrix multiplications), giving roughly 10x or more the throughput of CUDA cores. Q2. Memory: H200 has 141 GB HBM3e at 4.8 TB/s vs H100's 80 GB HBM3 at 3.35 TB/s. LLM token generation is memory-bandwidth-bound, and more capacity allows larger batches and KV caches, so throughput rises with the same Tensor Core compute. Q3. G = Grace CPU, B = Blackwell GPU, 200 = tier/generation, NVL72 = 72 GPUs in a single NVLink domain (rack-scale, liquid-cooled, with 36 Grace CPUs). Q4. QLoRA keeps the 4-bit base model at ~35 GB plus adapters and activations, so a single 80–96 GB GPU is enough: H100 / H100 NVL / H200, or RTX PRO 6000 Blackwell (96 GB); an L40S (48 GB) can work with care. No multi-node fabric is needed. Q5. (1) Scale-up NVLink/NVSwitch – GPU-to-GPU inside a node/rack; (2) scale-out compute fabric (InfiniBand or Spectrum-X Ethernet) – collective communication between nodes; (3) storage/front-end – data, checkpoints, user access; (4) management – provisioning, monitoring, out-of-band BMC. Q6. MIG – hardware partitions (up to 7 per GPU) with dedicated SMs, cache and memory, managed by the GPU Operator's MIG Manager in Kubernetes. Time-slicing would not give isolation or guarantees. Scoring tip: 5–6 correct = ready for the next course level; under 4 = revisit Module 1 and the sizing slide.

## Slide 42: Questions and discussion
THANK YOU
Further reading for participants:
NVIDIA architecture whitepapers: Hopper (H100) and Blackwell
NVIDIA DGX SuperPOD and BasePOD reference architectures
NVIDIA GPU Operator and DCGM documentation
CUDA C++ Programming Guide: hardware implementation chapter
NVIDIA datasheets for current GPU specifications
Notes: CLOSING & Q&A (10 min) Thank participants. Open the floor for questions; revisit any flip-chart questions not yet answered. Point participants to the further reading: • Architecture whitepapers (Hopper, Blackwell) for the full details on SMs, Tensor Cores and memory. • DGX SuperPOD / BasePOD reference architectures for real cluster designs (network, storage, power numbers). • GPU Operator and DCGM docs for Kubernetes and monitoring. • CUDA C++ Programming Guide for those who want to understand how code maps to SMs and warps. • Always use current datasheets for specifications – values in this deck are approximate and the product line changes quickly. Suggested follow-up sessions: hands-on lab with the GPU Operator on Kubernetes, LLM inference optimization with NIM/TensorRT-LLM, and fine-tuning with NeMo. Ask participants to complete the course feedback form.